## Slide 1: X3-Hybrid G4 5.0kW/6.0kW/8.0kW/10.0kW/12.0kW/15.0kW
Safe
IP65 protection level Integrated SPD
Intelligent
150% EPS overload output for 10s Switchover time <10ms
Lithium-ion & Lead-acid battery compatible CT compatible, loads respond within 0.3s
Intelligent loads management (e.g., Heat pump) On & Off-grid parallel function, up to 150kW
5 work modes, 2 charging periods available VPP ready, ancillary service in power market
Three-phase unbalanced output Maximum 5kW output power on single phase at most
Super-backup ready, EPS operation without batteries
Economic
16A DC single string input current, support high power solar panel Up to 150% PV input
Store the surplus energy from PV to battery
Low start output voltage makes inverter longer working time Less energy loss on battery to inverter
Dual peak limit value, flexible optimization of electricity bills
High-eﬃcient
200% PV oversized and up to 110% AC overload output Higher efficiency on charging and discharging, up to 97.5% Built-in shadow tracking function
Features
Three-phase Hybrid inverter
X
OLA
S
POWERING A GREEN FUTURE
V2.9 Information may be subject to modify without notice.
650.00010.00
info@solaxpower.com service@solaxpower.com
AU: +61 1300 476 529
DE: +49 (0) 6142 4091 664
UK: +44 2476 586998
NED:+31 (0) 8527 37932
Global: +86 571-56260008
PL: +48 662 430 292
www.solaxpower.com
CIRCUIT DIAGRAM
DC Switch
﹢
PV1
PV2
-
﹢
﹣
DC EMI
Filter
MPPT1
(Boost1)
MPPT2
(Boost2)
﹢
BAT
﹣
DC EMI
Filter
DC/DC
DC BUS
DC/AC
AC
Filter
AC EMI
AC
Relay
EPS
Relay
EPS EMI
DC SPD
Bypass
Relay
AC SPD
L1
L2
L3
N PE
Grid
L1
L2
L3 N
EPS
(Off grid)

## Slide 2: X3-HYBRID G4 (THREE PHASE)
STANDARD
Safety
EMC
Certification
BATTERY DATA
Battery type
Battery voltage range [V]
Max. continuous charge / discharge current [A]
Nominal AC voltage [V]
Nominal grid frequency [Hz]
Displacement power factor
THDi (rated power) [%]
Nominal output power [W]
Peak apparent power [VA]
Max.continous current [A]
Nominal voltage [V]; Frequency [Hz]
Switch time [ms]
Parallel operation
SYSTEM DATA
Max. eMciency [%]
Euro. eMciency [%]
Battery charge / discharge effciency [%]①
Degree of protection
Operating temperature range [°C]
Max. operation altitude [m]
Relative humidity [%]
Typical noise emission [dB]
Storage temperature [°C]
Dimensions (W×H×D) [mm]
Net weight [kg]
Cooling concept
Communication interfaces
415 / 240; 400 / 230; 380 / 220
50 / 60
0.8 leading ~ 0.8 lagging
< 3
Lithium-ion battery / Lead-acid Battery
180 ~ 800
30
98.0
97.7
98.5 / 97.5
IP65
-35 ~ +60 (Derating above +45)
< 3000
4~100 (condensing)
-40 ~ +70
503 × 503 × 199
30
5000
12000, 10s
7.2
6000
12000, 10s
8.7
8000
18000, 10s
11.6
10000
18000, 10s
14.5
12000
22500, 10s
17.5
400 / 230; 50 / 60
< 10
YES
15000
22500, 10s
21.8
< 35
< 45
EN/IEC62109-1 / -2
POWER CONSUMPTION
Internal consumption (night) [W]
< 40W for standy, < 5W for idle
VDE4105, G99, G98, AS4777, EN50549, CEI 0-21, IEC61727, PEA / MEA, NRS-097-2-1, RD1699, TOR
EN61000-6-1 / 2 / 3 / 4; EN61000-3-2 / 3 / 11 / 12
EPS(OFF-GRID OR BACK-UP) OUTPUT (WITH BATTERY)
X3-HYBRID-5.0-D |  |  | X3-HYBRID-6.0-D |  | X3-HYBRID-8.0-D |  | X3-HYBRID-10.0-D |  | X3-HYBRID-12.0-D |  | X3-HYBRID-15.0-D | 
DC INPUT |  |  |  |  |  |  |  |  |  |  |  | 
Max. PV array power [Wp] |  | 10000 |  | 12000 |  | 16000 |  | 20000 |  | 24000 |  | 30000
Max. PV input voltage [V] |  | 1000 |  | 1000 |  | 1000 |  | 1000 |  | 1000 |  | 1000
Start output voltage [V] |  | 200 |  | 200 |  | 200 |  | 200 |  | 200 |  | 200
Nominal input voltage [V] |  | 640 |  | 640 |  | 640 |  | 640 |  | 640 |  | 640
MPP voltage range [V] |  | 180 ~ 950 |  | 180 ~ 950 |  | 180 ~ 950 |  | 180 ~ 950 |  | 180 ~ 950 |  | 180 ~ 950
No. of MPP trackers / Strings per MPP tracker |  | 2 (1 / 1) |  | 2 (1 / 1) |  | 2 (2 / 1) |  | 2 (2 / 1) |  | 2 (2 / 1) |  | 2 (2 / 1)
Max. input current (input PV1 / input PV2) [A] |  | 16 / 16 |  | 16 / 16 |  | 28 / 16 |  | 28 / 16 |  | 28 / 16 |  | 28 / 16
Max. short circuit current (input PV1 / input PV2) [A] |  | 20 / 20 |  | 20 / 20 |  | 35 / 20 |  | 35 / 20 |  | 35 / 20 |  | 35 / 20
AC INPUT & OUTPUT |  |  |  |  |  |  |  |  |  |  |  | 
Nominal AC output power [W] |  | 5000 |  | 6000 |  | 8000 |  | 10000 |  | 12000 |  | 15000
Max. AC output apparent power [VA] |  | 5500 |  | 6600 |  | 8800 |  | 11000 |  | 13200 |  | 15000
Max. AC output current [A] |  | 8.1 |  | 9.7 |  | 12.9 |  | 16.1 |  | 19.3 |  | 24.1
Nominal AC input apparent power [VA] |  | 10000 |  | 12000 |  | 16000 |  | 20000 |  | 20000 |  | 20000
Max. AC input apparent power [VA] |  | 10000 |  | 12000 |  | 16000 |  | 20000 |  | 22000 |  | 22000
Nature cooling Smart cooling
CT / Meter (optional), External control RS485, Pocket WiFi (Optional: Pocket Lan / 4G), DRM, USB Upgrade, NTC (optional)
EFFICIENCY CURVE
DERATING CURVE
Derating Curve(15kW)
0
30
2
4
6
8
10
12
14
16
35
40
45
55
60
65
70
50
Temperature(°C)
380-550V
550-950V
20% 30%
Percentage of output power
88.5
89.5
90.5
91.5
92.5
93.5
94.5
95.5
96.5
97.5
5%
0%
10%
50%
75%
100%
330V
380V
430V
480V
530V
580V
630V
680V
720V
800V
Power/kW
Eonversion Efficiency
0
15000 15000 | 15000 15000 | 15000 15000 | 15000 15000 | 15000 |  |  | 
 |  |  | 13500 |  | 12000 |  | 
 |  |  |  | 10500 |  |  | 
 |  |  |  |  | 7500 | 7500 | 
 |  |  |  |  |  | 4500 | 4500
 |  |  |  |  |  |  | 0
X3-HYBRID-5.0-D X3-HYBRID-6.0-D X3-HYBRID-8.0-D X3-HYBRID-10.0-D
X3-HYBRID-12.0-D
X3-HYBRID-15.0-D
PROTECTION
Anti-Islanding protection
DC reverse polarity protection
Insulation monitoring
Residual current monitoring
AC overcurrent protection
AC short-circuit protection
AC overvoltage protection
AFCI
Surge protection
Yes
Yes
Yes
Yes
Yes
Yes
Yes
OPT
Type II, DC and AC
①: PV to BAT Max. eMciency 98.5%, BAT to AC Max. eMciency 97.5%.